Center to end distance of the elbow

- The standard radius of the elbow as per ASME B16.9 is two types

- long radius

- short radius

- long radius means the radius of the center line circle of the elbow is 1.5*D (where D is the nominal pipe size)

- short radius means the radius of the center line circle of the elbow is 1*D (where D is the nominal pipe size)

- to calculate the center to end distance for elbow with any angle (θ°elbow ) consider  figure 1 (shown below)

a: the center to end distance of the elbow (to be calculated)

R: The radius of the elbow

θ: the elbow angle

tan (θ/2)= a/R

a = R * tan (θ/2)

in case of long radius R = 1.5 * D

So,  a = 1.5 D * tan (θ/2)

NOTES:

- θ in degrees

- D in inches

- In case of elbow 90° the equation will be simplified to  (a = 1.5*D )

- To convert “a “ to SI units multiply by 25.4

Figure 1